## Slide 1: OPC UA and EPICS Introduction
Ralph Lange
ITER IO – Control System Division
EPICS Collaboration Meeting, 12-17 Nov 2018, Melbourne

## Slide 2: History (I): OPC and OPC UA
1996: OPC (Classic) = OLE for Process Control
  Based on COM/DCOM, only on Microsoft Windows
  Complex security configuration (access lists)
  Uses many ports (not firewall friendly)
  Absolute addressing
2006: OPC UA = OPC Unified Architecture
  Superset of OPC Classic services
  Open network protocols
  Certificate based security
  Symbolic addressing

## Slide 3: History (II): EPICS OPC Classic Support
Upstream Author: Bernhard Kuner (HZB / BESSY II) (first release ~ 2004)
Based on commercial client SDK (SoftIng)
  APIs were often changed (complete rewrite necessary)
Only on Windows
  Hard to support multiple versions of Windows and Compilers
License model allows free distribution of binaries: Windows IOC downloadable
Approx. 10 users, robust, scalable
http://www-csr.bessy.de/control/SoftDist/OPCsupport/

## Slide 4: Why OPC UA?
Industrial standard that is gaining ground: servers for more and more devices available
Symbolic addressing: PLC side may change as long as the names stay (IOC does not even have to reboot)
Single TCP connection: WAN capable
Security: certificate based authentication, encrypted transport
Browsing: powerful free GUI clients available
Server logically on top of device: status variables in standard namespace provided even if device is off

## Slide 5: EPICS Support for S7 PLCs
s7plc: Block read/write on TCP/IP
  Only complete DBs, raw data (no timestamps)
  PLC program has to actively send and receive data
  High performance
s7nodave: S7 native protocol
  Reverse-engineered native Siemens protocol
  Only single data items
  No PLC programming (handled by PLC firmware)
  Low performance
Both use byte-offset-into-data-block addressing

## Slide 6: OPC UA on S7 PLCs
Symbolic addressing
  All items are found by name
  PLC side may change – even without IOC reboot
Wide range of scalar types, arrays and structures
  Supports everything from single data items to complete DBs
  Server and device timestamps available
Support in TIA Portal
  No programming, just checking a box
Embedded OPC UA server on S7-1500 series PLCs
  Medium to high performance (varies with CPU type)

## Slide 7: OPC UA Basics (Object Model)
Current Scope

## Slide 8: OPC UA Basics (Connection Model)
EPICS Record
Device Support
Not Implemented Yet

## Slide 9: OPC UA Basics (Subscription Model)

## Slide 10: OPC UA Support Prototype (2017-2018)
Upstream Author: Bernhard Kuner (HZB / BESSY II)
Based on commercial SDK by Unified Automation
  API fits EPICS Device Support Architecture
  UaExpert client application (same vendor) is widely used
  Binaries can be distributed royalty-free
Runs on Windows and Linux
Some limitations:
  No support for structures, only basic array support
  Scaling issues when going >1000 items
https://github.com/bkuner/opcUaUnifiedAutomation

## Slide 11: OPC UA Use Cases at ITER
Original scope: connect to central interlock functions via WinCC-OA (< 100 variables, read-only)
Fusion for Europe (F4E) are pushing for OPC UA to connect to Siemens S7-1500 series PLC
  F4E wants to use OPC UA for the next bunch of building management I&C
Functional and performance testing at F4E and Tata Consulting (India), using patched prototype
  Tests started 2017 -> Decision taken in early 2018

## Slide 12: Block R/W vs. OPC UA @1516 (20kB)
Chart: Minimum Cycle Time (ms) + CPU load (ms)
| 0 | 0 (+ 40 ms load) | 5 | 10 | 50 | 50 (+ 40 ms load)
Change Rate (20% of CodacStates) | 8 | 253 | 30 | 60 | 300 | 300
Change Rate (40% of CodacStates) | 8 | 251 | 30 | 60 | 300 | 300
Change Rate (80% of CodacStates) | 8 | 254 | 30 | 60 | 300 | 300
Change rate (100% of CodacStates) | 8 | 254 | 30 | 60 | 300 | 300
Change Rate(20% of CodacStates_OPCUA) | 287.67 | 277.33 | 200 | 200 | 200 | 213.66
Change Rate(40% of CodacStates_OPCUA) | 203.93 | 200 | 200 | 200 | 200 | 202.6
Change Rate(80% of CodacStates_OPCUA) | 271.69 | 200 | 201.12 | 200 | 200 | 227.1
Change Rate(100% of CodacStates_OPCUA) | 274.9 | 201.3 | 200 | 200 | 200 | 203.74

## Slide 13: Block R/W vs. OPC UA @1518 (32kB)
Chart: Minimum Cycle Time (ms) + CPU load (ms)
| 0 | 0 (+ 40 ms load) | 5 | 10 | 50 | 50 (+ 40 ms load)
Change Rate (20% of CodacStates_SPSS) | 37 | 242.09 | 44.04 | 60.05 | 300.05 | 300.05
Change Rate(20% of CodacStates_OPC) | 100 | 100 | 100.17 | 100 | 100 | 100
Change Rate (40% of CodacStates_SPSS) | 36.57 | 242.91 | 42.73 | 60.05 | 300.05 | 300.05
Change Rate(40% of CodacStates_OPC) | 100 | 100 | 100 | 100 | 100 | 100
Change Rate (80% of CodacStates_SPSS) | 37.07 | 244.53 | 44.87 | 60.05 | 300.05 | 300.05
Change Rate(80% of CodacStates_OPC) | 100 | 100 | 100 | 100 | 100 | 100
Change rate (100% of CodacStates_SPSS) | 37.71 | 245.34 | 44.74 | 60.05 | 300.05 | 300.05
Change Rate(100% of CodacStates_OPC) | 100 | 100 | 100 | 100 | 100 | 100

## Slide 14: S7-1500 Limitations
TIA Portal V14: Few thousand items up to 10K@1518 100ms update 200ms publishing (50/100 @1518)
TIA Portal V15: 50K items up to 200K@1518 100ms update 500ms publishing (10/10 @1518)
1000 monitored items (10K @1518)
Single item subscriptions do not scale Use of structures and arrays is up to 100x faster

## Slide 15: Current Status of Support
Scalar data types and usual record types supported
  Boolean, signed and unsigned integers, double, string
  ai/ao, bi/bo, mbbi/mbbo, mbbiDirect/mbboDirect, longin/longout, stringin/stringout, lsi/lso
Still missing:
  Support for structures
  Support for arrays
  Support for remote procedures
  Status details and health monitoring
https://github.com/ralphlange/opcua
  Feedback and contributions welcome!

## Slide 16: Roadmap
Feature-complete release until end of 2018
Still need to think about workflow that allows changes and merges with configuration tools/databases
For ITER, OPC UA is a promising candidate to replace the traditional S7 interface
  Will have to continue support for s7plc because of S7-300 and redundant PLC systems

## Slide 17: So…
SDK source code license is ~3.5k€ incl. 1 year support
Development help would be useful
  Bug fixes
  Robustness
  Tests
What do you think?
What is missing?
What are the next steps?